## TEMPLE PLUMBING FIXTURE SCHEDUL
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11
PLUMBING FIXTURE SCHEDULE
ID | COUNT | FIXTURE | NOTES | CW | HW | W | V | IMAGE | SPECIFICATION
CS-1 | 1 | CLOSET SINK |  | 1/2 | 1/2 | 2 | 1-1/2 | CS-1 Kohler K-5964.jpg | KOHLER MAYFIELD K-5964 SINGLE 22" X 15" X 7-3/4" BOWL, COUNTER MOUNT SINK. CHICAGO FAUCET 201-G8AE3-317AB DECK MOUNTED MANUAL SINK FAUCET WITH 8" CENTERS AND 4" WRISTBLADE HANDLES.
DF-1 | 7 | DRINKING FOUNTAIN |  | 1/2 | -.- | 2 | 1-1/2 |  | ELKAY EDFPB117C SWIRLFLO BI-LEVEL FOUNTAIN, NON-FILTERED, NON-REFRIGERATED STAINLESS STEEL WALL MOUNT DRINKING FOUNTAIN WITH FLEXI-GUARD SAFETY BUBBLER. CHILLED WATER SUPPLIED FROM REMOTE CHILLER, SEE PLANS FOR LOCATIONS. SEE ARCHITECTURAL FOR MOUNTING HEIGHTS.
DF-2 | 2 | DRINKING FOUNTAIN | BI-LEVEL | 1/2 | -.- | 2 | 1-1/2 | DF-2 Elkay EZSTL8LC.png | ELKAY EZSTL8LC WALL MOUNTED, BI-LEVEL, BARRIER FREE ELECTRIC WATER COOLER WITH FLEXIBLE BUBBLER GUARD, STAINLESS STEEL BOWLS, REMOVABLE FRONT LOUVERED VENTILATING GRILL, AND CONTROL BUTTONS ON FRONT; 1/5 HP, 115V/1Φ/60HZ WITH CHILLING CAPACITY OF 8.0 GPH
DF-3 | 2 | DRINKING FOUNTAIN |  | 1/2 | -.- | 2 | 1-1/2 | DF-3 Elkay EDFPBM114K.png | ELKAY EDFPBM114K SWIRLFLO SINGLE FOUNTAIN, WALL MOUNT, NON-FILTERED, NON-REFRIGERATED STAINLESS STEEL DRINKING FOUNTAIN WITH FLEXI-GUARD SAFETY BUBBLER. CHILLED WATER SUPPLIED FROM REMOTE CHILLER, SEE PLANS FOR LOCATIONS. SEE ARCHITECTURAL FOR MOUNTING HEIGHTS.
DSN-1 | 4 | DOWNSPOUT NOZZLE |  | -.- | -.- | SEE PLANS | -.- | DSN-1 JRS-1770.jpg | J. R. SMITH FIGURE 1770Y CAST BRONZE DOWNSPOUT NOZZLE AND FLANGE WITH NO-HUB OUTLET. MATCH OUTLET SIZE TO PIPE SIZE SHOWN ON PLANS
EW-1 | 5 | EMERGENCY EYE WASH |  | 1/2 | 1/2 | -.- | -.- | EW-1 Guardian G1825.jpg | GUARDIAN G1825 PEDESTAL MOUNTED STAINLESS STEEL EYEWASH WITH G3600LF THERMOSTATIC MIXING VALVE OPTION MOUNTED BELOW BOWL. EYEWASH MEETS ANSI Z.358.1
EW-2 | 1 | EMERGENCY EYE WASH |  | 1/2 | 1/2 | -.- | -.- | EW-2 GUARDIAN G1805.jpg | GUARDIAN G1805 EYEWASH STATION, DECK MOUNTED AUTOFLOW SWIVEL, RIGHT HAND MOUNTING, GENTLE SPRAY OUTLET HEADS WITH FLIP-TOP DUST COVERS MOUNTED ON CHROME PLATED BRASS SUPPLY ARMS. EYEWASH MEETS ANSI Z358.1.
F-1 | 1 | FONT |  | -.- | -.- | -.- | -.- |  | SEE FONT FITTING SCHEDULE ON SHEET P701
F-2 | 2 | FONT |  | -.- | -.- | -.- | -.- |  | SEE FONT FITTING SCHEDULE ON SHEET P701
F-3 | 1 | FONT |  | -.- | -.- | -.- | -.- |  | SEE FONT FITTING SCHEDULE ON SHEET P701
F-4 | 1 | FONT |  | -.- | -.- | -.- | -.- |  | SEE FONT FITTING SCHEDULE ON SHEET P701
FD-1 | 35 | FLOOR DRAIN |  | -.- | -.- | 2 | 1-1/2 | FD-1 JR SMITH 2005.jpg | J. R. SMITH FIGURE 2005Y-BH FLOOR DRAIN WITH 9" DIAMETER CAST IRON BODY AND FLASHING, 5" SQUARE NICKEL BRONZE ADJUSTABLE STRAINER HEAD, NO-HUB OUTLET, VANDAL PROOF SCREWS, AND SQUARE HINGED GRATE.
FD-2 | 9 | FLOOR DRAIN |  | -.- | -.- | 4 | 2 | FD-2 JR SMITH 2110.jpg | J. R. SMITH FIGURE 2110Y FLOOR DRAIN WITH 12" DIAMETER CAST IRON BODY AND FLASHING COLLAR, 8-1/2" ROUND CAST IRON GRATE, NO-HUB OUTLET, AND VANDAL PROOF SCREWS.
FD-3 | 3 | FLOOR DRAIN |  | -.- | -.- | -.- | -.- | FD-2 JR SMITH 2110.jpg | J. R. SMITH FIGURE 2110Y-B FLOOR DRAIN WITH 12" DIAMETER CAST IRON BODY AND FLASHING COLLAR, 8-1/2" ROUND CAST IRON GRATE, NO-HUB OUTLET, VANDAL PROOF SCREWS, AND SEDIMENT BUCKET. MATCH OUTLET SIZE TO PIPE SIZE SHOWN ON PLANS.
FS-1 | 13 | FLOOR SINK |  | -.- | -.- | 4 | 2 | FS-1 JR SMITH 3200.jpg | J. R. SMITH FIGURE 3200Y CAST IRON 18" SQUARE 12" DEEP RECEPTOR FLOOR SINK WITH SEEPAGE HOLES, ACID RESISTANT COATED INTERIOR, NICKEL BRONZE RIM AND SECURED 16-1/2" SQUARE GRATE, ALUMINUM DOME BOTTOM STRAINER, NO-HUB OUTLET, AND VANDAL PROOF SCREWS.
HB-1 | 1 | HOSE BIBB |  | 1/2 | -.- | -.- | -.- | HB-1 CHICAGO 293-CP.jpg | CHICAGO FAUCET FITTING NO. 293 RFC WALL FAUCET WITH CHROME PLATE FINISH, 3/4" MALE HOSE THREAD, 2-1/4" TEE HANDLE, AND E27 VACUUM BREAKER
ICE-1 | 2 | WATER CONNECTION |  | 1/2 | -.- | -.- | -.- | ICE-1 IPS AB9700HA.jpg | IPS AB9700HA WATER OUTLET BOX WITH QUARTER TURN LEAD FREE ARRESTER VALVE AND INTEGRAL WATER HAMMER ARRESTOR.
IS-1 | 14 | INSTRUCTION ROOM SINK | PEDESTAL MOUNTED | 1/4 | -.- | 1-1/4 | 1-1/4 | IS-1 ZURN Z821CO.jpg | TIFFANY MARBLE SINK WITH ZURN Z821AO DECK MOUNTED, CHROME-PLATED, RIGID 3-1/2" GOOSENECK SPOUT AND KOHLER K-8820-CP DRAIN.
L-1 | 25 | LAVATORY | RESTROOM | 1/2 | 1/2 | 1-1/2 | 1-1/2 | L-2 KOHLER K-1722_American Standard faucet.png | KOHLER K-2210 CAXTON WHITE VITREOUS CHINA UNDERMOUNT SINK WITH 19-1/2"L X 16-1/4"W X 10-3/4"D OVAL BOWL AND OVERFLOW WITH K-7129-A OPEN GRID STRAINER AND DRAIN. FAUCET: AMERICAN STANDARD 775B.305 (NEXTGEN SELECTRONIC) TOUCH FREE FAUCET, PRESSURE COMPENSATING AND VANDAL RESISTENT NON-AERATING SPRAY OUTLET, 0.5 GPM, HARD WIRED SENSOR, INTEGRAL THERMOSTATIC HOT WATER MIXER CERTIFIED TO ASSE 1070 AND SET TO 105°F DISCHARGE TEMPERATURE, REMOVABLE MIXING HANDLE, COMES WITH BRAIDED STAINLESS STEEL HOSES. PROVIDE SLOAN ETF-470-A CHECK VALVES IN HOT AND COLD SUPPLIES, LOOSE KEY ANGLE STOPS, AND CHROME PLATED 17 GAUGE CAST BRASS P-TRAP WITH CLEANOUT PLUG. COVER ALL EXPOSED PIPING WITH WHITE "HANDI-LAV GUARD" AS REQUIRED FOR ADA COMPLIANCE.
L-2 | 6 | LAVATORY | RESTROOM | 1/2 | 1/2 | 1-1/2 | 1-1/2 | L-2 KOHLER K-1722_American Standard faucet.png | KOHLER CHESAPEAKE K-1722 VITREOUS CHINA, 19-1/4" X 17-1/4" WALL MOUNT LAVATORY WITH SINGLE FAUCET HOLE. FAUCET: AMERICAN STANDARD 775B.305 (NEXTGEN SELECTRONIC) TOUCH FREE FAUCET, PRESSURE COMPENSATING & VANDAL RESISTENT NON-AERATING SPRAY OUTLET, 0.5 GPM, HARD WIRED SENSOR, INTEGRAL THERMOSTATIC HOT WATER MIXER CERTIFIED TO ASSE 1070 AND SET TO 105°F DISCHARGE TEMPERATURE, REMOVABLE MIXING HANDLE, COMES WITH BRAIDED STAINLESS STEEL SUPPLY HOSES. PROVIDE WITH SLOAN ETF-470-A CHECK VALVES IN HOT AND COLD SUPPLIES, LOOSE KEY ANGLE STOPS, AND CHROME PLATED 17 GAUGE CAST BRASS P-TRAP WITH CLEANOUT PLUG. COVER ALL EXPOSED PIPING WITH WHITE "HANDI-LAV GUARD" AS REQUIRED FOR ADA COMPLIANCE
NFH-1 | 2
NFH-2 | 3 | NON-FREEZE GROUND HYDRANT | EXTERIOR | 3/4 | -.- | -.- | -.- | NFH-2 JR SMITH 5810.jpg | J. R. SMITH FIGURE 5810 NON-FREEZE GROUND HYDRANT WITH STAINLESS STEEL BOX AND FULL HINGED COVER, QUARTER TURN LOOSE KEY.
RD-1 | 40 | ROOF DRAIN |  | -.- | -.- | SEE PLANS | -.- | RD-1 JR SMITH 1010.jpg | J. R. SMITH FIGURE 1010Y ROOF DRAIN WITH CAST IRON BODY, COMBINED FLASHING CLAMP, GRAVEL STOP, DOME, EXTENSION, SUMP RECEIVER, AND UNDERDECK CLAMP, MATCH OUTLET TO PIPE SIZE SHOWN ON PLANS.
RDO-1 | 40 | ROOF DRAIN OVERFLOW |  | -.- | -.- | SEE PLANS | -.- | RDO-1 JR SMITH FIGURE 1080.jpg | J. R. SMITH FIGURE 1080Y ROOF DRAIN WITH CAST IRON BODY, COMBINED FLASHING CLAMP, GRAVEL STOP, DOME EXTENSION, SUMP RECEIVER, UNDERDECK CLAMP, AND 2" HIGH WATER COLLAR. MATCH OUTLET SIZE TO SIZE SHOWN ON PLANS.
S-1 | 3 | SINK |  | 1/2 | 1/2 | 2 | 1-1/2 | S-1 ELKAY DLR3322101.png | ELKAY DLR3322101 LUSTERTONE CLASSIC 33" X 22" X 10-1/8", EQUAL DOUBLE BOWL DROP IN SINK, 18 GAUGE STAINLESS STEEL. FAUCET: CHICAGO 895-RGD2E1ABCP 5-1/4" RIGID GOOSENECK SPOUT, 2-3/8" LEVER HANDLES, POLISHED CHROME FINISH, 4" FIXED CENTER HOLES. TEMPERED WATER SUPPLIED FROM FLE480 THERMOSTATIC MIXING VALVE SET TO 105°F LOCATED BELOW SINK. PROVIDE WITH 17 GAUGE CAST BRASS P-TRAP WITH CLEANOUT PLUG, SLOAN ETF-470-A CHECK VALVES IN HOT AND COLD SUPPLIES, LOOSE KEY ANGLE STOPS, AND 20" LONG BRAIDED STAINLESS STEEL SUPPLIES.
S-2 | 2 | SINK |  | 1/2 | 1/2 | 2 | 1-1/2 | S-2 ELKAY DLR221910PD3.png | ELKAY DLR221910PD3 LUSTERSTONE CLASSIC SINGLE BOWL DROP-IN SINK WITH PERFECT DRAIN, 19 GAUGE STAINLESS STEEL, 18"L X 19-1/2"W X 10-1/8"D. FAUCET: CHICAGO 895-RGD2E1ABCP 5-1/4" RIGID GOOSENECK SPOUT, 2-3/8" LEVER HANDLES, POLISHED CHROME FINISH, 4" FIXED CENTER HOLES. TEMPERED WATER SUPPLIED FROM LFE480 THERMOSTATIC MIXING VALVE SET TO 105°F LOCATED BELOW SINK. PROVIDE WITH 17 GAUGE CAST BRASS P-TRAP WITH CLEANOUT PLUG, SLOAN ETF-470-A CHECK VALVES IN HOT AND COLD SUPPLIES, LOOSE KEY ANGLE STOPS, AND 20" LONG BRAIDED STAINLESS STEEL SUPPLIES.
SH-1 | 4 | SHOWER | BAPTISTRY | 1/2 | 1/2 | 2 | 1-1/2 | SH-1 CHICAGO SH-TP4-00-021.jpg | CHICAGO SH-TP4-00-021 SHOWER WITH THERMOSTATIC/PRESSURE BALANCING CARTRIDGE, 2.5 GPM HANDSPRAY, TWO 34" STAINLESS STEEL HOSES WITH AUTOMATIC HOSE DRAIN, 24" WALL-MOUNTED SIDE BAR WITH HAND SPRAY HOLDER, INTEGRAL SERVICE STOPS WITH SHOWER DRAIN CHECKS TO PREVENT CROSS FLOW. J. R. SMITH FIGURE 2005Y FLOOR DRAIN WITH 9" DIAMETER CAST IRON BODY AND FLASHING COLLAR WITH 5" SQUARE CHROME PLATED ADJUSTABLE HEAD, NO-HUB OUTLET, AND VANDAL PROOF SCREWS.
SS-1 | 9 | SERVICE SINK |  | 3/4 | 3/4 | 3 | 2 | SS-1 KOHLER K-6710.jpg | KOHLER K-6710 WHITBY 28" X 28" ENAMELED CAST IRON FLOOR-MOUNTED CORNER MODEL SERVICE SINK; K-9146 BRASS DRAIN AND STRAINER WITH 3" OUTLET; K-8940 REMOVABLE VINYL-COATED RIM GUARD. CHICAGO 897 FAUCET WITH VACUUM BREAKER, SCREWDRIVER STOPS IN SHANKS, 5' RUBBER HOSE, AND WALL HOOK 853
TD-1 | 1 | TRENCH DRAIN | LAUNDRY | -.- | -.- | 4 | 2 | <None> | H-M 25' L X 2' W X 1' D TRENCH DRAIN SYSTEM WITH REMOVABLE LID, LINT FILTER, AND SIDE DRAIN OUTLET.
TD-2 | 5 | TRENCH DRAIN | MECHANICAL ROOM | -.- | -.- | 4 | 2 | TD-2 JR SMITH 9812.jpg | J. R. SMITH FIGURE 9812-M 10" WIDE HIGH CAPACITY PRE-SLOPED FIBERGLASS TRENCH DRAIN SYSTEM WITH SLOTTED DUCTILE IRON GRATE.
TD-3 | 1 | TRENCH DRAIN | MECHANICAL YARD | -.- | -.- | 3 | 1-1-2 | TD-3 JR SMITH 2710.jpg | J. R. SMITH FIGURE 2710 HEAVY DUTY MODULAR TRENCH DRAIN WITH DUCCO CAST IRON FLANGED BODY, END PLATED, AND LOOSE SET SQUARE HOTE GRATE. GRATE TO BE TRAFFIC RATED.
U-1 | 4 | WALL MOUNTED, WASHDOWN, FLUSHOMETER | RESTROOM | 3/4 | -.- | 2 | 1-1/2 | U-1 KOHLER K-4991-ET.jpg | KOHLER K-4991-ET BARDON WHITE VITREOUS CHINA, WALL HUNG, 1 GPF WASHDOWN, HIGH-EFFICIENCY URINAL WITH 3/4" TOP SPUD. SLOAN CROWN 186 SMO-1.0-OR BATTERY POWERED, EXPOSED SENSOR, 1.0 GPF PISTON FLUSHOMETER WITH POLISHED CHROME FINISH. J. R. SMITH 0637 URINAL SUPPORT. REFER TO ARCHITECTURAL PLANS FOR MOUNTING HEIGHTS.
WC-1 | 6 | WALL MOUNTED, FLUSHOMETER, ADA | RESTROOM | 1 | -.- | 4 | 2 | WC-1,2 KOHLER K-4325.jpg | KOHLER K-4325 KINGSTON WHITE VITREOUS CHINA, WALL HUNG, 1.6 GPF SIPHON JET WATER CLOSET WITH ELONGATED BOWL AND TOP SPUD; K-4670-C LUSTRA ELONGATED OPEN FRONT SEAT IN WHITE. SLOAN CROWN 111 SMO-1.6-OR BATTERY POWERED, EXPOSED SENSOR, 1.6 GPF PISTON FLUSHOMETER WITH POLISHED CHROME FINISH INSTALLED WITH ACTUATOR ON WIDE SIDE OF FIXTURE. J. R. SMITH 0210Y ADJUSTABLE FIXTURE SUPPORT (LEFT, RIGHT, OR DOULE AS REQUIRED) WITH NO-HUB OUTLETS. MOUNT SO AS TO BE ADA COMPLIANT. REFER TO ARCHITECTUREAL PLAN FOR MOUNTING HEIGHTS.
WC-2 | 8 | WALL MOUNTED, FLUSHOMETER | RESTROOM | 1 | -.- | 4 | 2 | WC-1,2 KOHLER K-4325.jpg | KOHLER K-4325 KINGSTON WHITE VITREOUS CHINA, WALL HUNG, 1.6 GPF SIPHON JET WATER CLOSET WITH ELONGATED BOWL AND TOP SPUD; K-4670-C LUSTRA ELONGATED OPEN FRONT SEAT IN WHITE. SLOAN CROWN 111 SMO-1.6-OR BATTER POWERED, EXPOSED SENSOR, 1.6 GPF PISTON FLUSHOMETER WITH POLISHED CHROME FINISH INSTALLED WITH ACTUATOR ON WIDE SIDE OF FIXTURE. J. R. SMITH FIGURE 0210Y ADJUSTABLE FIXTURE SUPPORT (LEFT, RIGHT, OR DOUBLE AS REQUIRED) WITH NO-HUB OUTLETS. REFER TO ARCHITECTURAL PLANS FOR MOUNTING HEIGHTS.
WC-3 | 17 | FLUSH TANK | RESTROOM | 1 | -.- | 4 | 2 | WC-3 KOHLER K-3818.jpg | KOHLER K-3818 MEMOIRS CLASSIC WHITE VITREOUS CHINA, FLOOR MOUNTED, BOTTOM OUTLET, COMFORT HEIGHT, 1.6 GPF FLUSH TANK WATER CLOSET WITH ELONGATED BOWL; K-4670-C LUSTRA ELONGATED OPEN FRONT SEAT IN WHITE; K-7637-CP ANGLE SUPPLY WITH STOP WITH POLISHED CHROME FINISH.